FIRE FIGHTING - SPRINKLER SYSTEM

| TYPE | OCCUPANCIES | SPRINKER OPERATION AREA | AREA PER SPRINKLER | DISTANCE BETWEEN LINES | DISTANCE FROM WALL | FLOW & PRESSURE | DURATION | PIPE SCHEDULE mm; No. Of sprinklers. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| L.H | Residential, institutional, community halls, offices, hospitals, clubs, museums, restaurant seating areas theaters, libraries, etc. | 1500 ft2 (139m2) | <200 ft2 (18.6m2) | 15ft (4.6m) | >10cm | 500-700 gpm & 15psi | 50-60 min | 25; 2. 32; 3. 40; 5. 50; 10. 65; 30. 80; 60. 100; 100. 150; 150. |
| O.H.G-1 | Parking’s, show rooms, dairy products manufacturing & processing, glass products manufacturing, laundries, restaurant service areas | 1500 ft2 (139m2) | <130 ft2 (12.1m2) | 15ft (4.6m) | >10cm | 700-1000 gpm & 15psi or high | 60-90 min | 25; 2. 32; 3. 40; 5. 50; 10. 65; 20. 80; 40. 100; 100. 150; 150. |
| O.H.G-2 | Mills, manufacturing, garages, machine shops etc. | 1500 ft2 (139m2) | <130 ft2 (12.1m2) | 15ft (4.6m) | >10cm | 800-1500 gpm & 15psi or high | 60-90 min | Same as O.H.G.-1 |
| E.H.G | Printing, metal processing, rubber manufacturing, saw mills etc. | 2900 ft2 (232m2) | <90 ft2 (8.4m2) | 12ft (3.7m) | >10cm | ----- | ---- | 25; 1. 32; 2. 40; 5. 50; 8. 65; 15. 80; 27. 100; 55. 150; 90. |

Eng.Atef A.Adawey